## ASHRAE Variables
Calgary International Airport ASHRAE Handbook Climatic Variables Future Projections
Calgary International Airport |  | Model Past |  | 2020s Future |  | 2020s Change |  | 2050s Future |  | 2050s Change |  | 2080s Future |  | 2080s Change
Variable | Units | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th% | Average | 10th%-90th%
ASHRAE Heating and Humidification Design Conditions
Heating Dry-Bulb 99.6% | °C | -31.3 | (-32 to -30.8) | -28 | (-29.4 to -27.2) | 3.3 | (1.5 to 4.6) | -25.8 | (-27.2 to -23.5) | 5.5 | (3.8 to 8) | -21.9 | (-24 to -20.2) | 9.4 | (7.5 to 11.8)
Heating Dry-Bulb 99.0% | °C | -29.4 | (-29.8 to -29.1) | -26.2 | (-27.5 to -25.3) | 3.3 | (1.9 to 4.3) | -23.9 | (-25.3 to -21.9) | 5.5 | (4.3 to 7.8) | -20.2 | (-22.3 to -18.4) | 9.2 | (7.1 to 11.3)
Dew Point 99.6% | °C | -29.2 | (-31.6 to -27.5) | -27 | (-29.1 to -24.5) | 2.2 | (1.3 to 3.1) | -25.5 | (-29.3 to -22.1) | 3.6 | (1.7 to 5.8) | -25.1 | (-27.9 to -22.4) | 4.1 | (1.1 to 6.2)
Humidity Ratio 99.6% | g/kg | 0.4 | (0.3 to 0.4) | 0.5 | (0.4 to 0.6) | 0.1 | (0 to 0.1) | 0.5 | (0.4 to 0.7) | 0.2 | (0.1 to 0.3) | 0.6 | (0.4 to 0.7) | 0.2 | (0 to 0.3)
MCDB (Dew point 99.6%) | °C | -2.2 | (-2.4 to -2.1) | -0.6 | (-1 to -0.2) | 1.6 | (1.1 to 2.2) | 1 | (0 to 2) | 3.2 | (2 to 4.4) | 3.2 | (1.5 to 4.5) | 5.4 | (3.5 to 6.8)
Cold Windspeed 99.6% | m/s | 7.9 | (4.9 to 10.5) | 8.2 | (4.8 to 11.4) | 0.2 | (-0.2 to 0.4) | 8.2 | (4.7 to 11.6) | 0.3 | (-0.4 to 0.5) | 8.2 | (4.8 to 11.4) | 0.2 | (-0.3 to 0.4)
MCDB (Windspeed 99.6%) | °C | -2.4 | (-2.5 to -2.2) | -0.7 | (-1 to -0.2) | 1.7 | (1.2 to 2.3) | 0.9 | (0 to 1.9) | 3.3 | (2.1 to 4.5) | 3.1 | (1.5 to 4.5) | 5.5 | (3.6 to 6.9)
MCWS (Dry-bulb 99.6%) | m/s | 3 | (1.9 to 4.1) | 3.2 | (2 to 4.5) | 0.1 | (-0.1 to 0.2) | 3.2 | (1.9 to 4.5) | 0.1 | (-0.1 to 0.3) | 3.2 | (1.9 to 4.5) | 0.1 | (-0.1 to 0.2)
PCWD (Dry-bulb 99.6%) | ° | 201 | (175 to 223) | 200 | (175 to 222) | 0 | (-2 to 1) | 201 | (175 to 222) | 0 | (-2 to 3) | 201 | (174 to 223) | 0 | (-2 to 3)
ASHRAE Cooling, Dehumidification and Enthalpy Design Conditions
Cooling Dry-Bulb 0.4% | °C | 30.3 | (30 to 30.7) | 32.4 | (31.5 to 33.3) | 2.1 | (1.3 to 3.2) | 35.1 | (33.7 to 37.3) | 4.8 | (3 to 7.2) | 38 | (34.8 to 41.4) | 7.7 | (4.9 to 11.2)
Cooling Dry-Bulb 1.0% | °C | 29.4 | (29 to 29.8) | 31.5 | (30.4 to 32.3) | 2 | (1.1 to 3.1) | 34 | (32.4 to 36.1) | 4.6 | (2.8 to 7) | 37 | (33.7 to 40.6) | 7.6 | (4.6 to 11.1)
Cooling Wet Bulb 0.4% | °C | 21.3 | (21.1 to 21.5) | 23.2 | (22 to 23.8) | 1.9 | (1.2 to 2.6) | 25.4 | (23.5 to 26.9) | 4.1 | (2.8 to 5.6) | 28 | (24.8 to 30.8) | 6.7 | (3.5 to 9.4)
Cooling Wet Bulb 1.0% | °C | 20.6 | (20.4 to 20.9) | 22.5 | (21.2 to 23.3) | 1.9 | (1 to 2.5) | 24.6 | (22.6 to 26.1) | 4 | (2.3 to 5.6) | 27.3 | (24.1 to 30) | 6.7 | (3.5 to 9.4)
MCDB (Wet Bulb 0.4%) | °C | 30.2 | (29.8 to 30.7) | 32.4 | (31 to 33.5) | 2.1 | (1.3 to 3.1) | 35.1 | (33.6 to 37.5) | 4.9 | (3 to 7.1) | 37.9 | (34.1 to 41.4) | 7.7 | (4.9 to 11.2)
MCDB (Wet Bulb 1.0%) | °C | 29.9 | (29.5 to 30.4) | 32 | (30.6 to 33) | 2.1 | (1.2 to 3.2) | 34.6 | (33 to 36.9) | 4.7 | (2.9 to 7) | 37.5 | (33.9 to 41) | 7.6 | (4.9 to 10.9)
MCWB (Dry-bulb 0.4%) | °C | 21.1 | (20.8 to 21.5) | 23.1 | (22.1 to 23.8) | 1.9 | (1.3 to 2.7) | 25.4 | (23.4 to 27) | 4.2 | (2.9 to 5.7) | 27.9 | (24.8 to 30.7) | 6.7 | (3.8 to 9.3)
MCWB (Dry-bulb 1.0%) | °C | 20.8 | (20.5 to 21.1) | 22.7 | (21.5 to 23.5) | 1.9 | (1.3 to 2.7) | 24.9 | (22.9 to 26.6) | 4.2 | (2.9 to 5.8) | 27.6 | (24.5 to 30.5) | 6.8 | (3.9 to 9.5)
MCWB (Dry-bulb 2.0%) | °C | 20.2 | (20 to 20.6) | 22.1 | (20.9 to 22.9) | 1.9 | (1.2 to 2.6) | 24.3 | (22.2 to 26) | 4.1 | (2.5 to 5.8) | 27 | (23.8 to 29.8) | 6.8 | (3.8 to 9.5)
Dew Point 0.4% | °C | 16.5 | (14.6 to 18) | 17.6 | (15.6 to 19) | 1 | (0.5 to 1.6) | 18.1 | (16.1 to 19.7) | 1.6 | (1.2 to 2) | 18.4 | (16.4 to 20.3) | 1.8 | (1.1 to 2.2)
Dew Point 1.0% | °C | 16.5 | (14.6 to 18) | 17.6 | (15.6 to 19) | 1 | (0.5 to 1.6) | 18.1 | (16.1 to 19.7) | 1.6 | (1.2 to 2) | 18.4 | (16.4 to 20.3) | 1.8 | (1.1 to 2.2)
MCDB (Dew point 0.4%) | °C | 26.2 | (25.3 to 26.8) | 24.7 | (23.1 to 26) | -1.5 | (-3.2 to 0.1) | 26.7 | (24.2 to 28.9) | 0.5 | (-2.8 to 2.3) | 30.1 | (26.9 to 33.8) | 3.9 | (0.2 to 7.1)
MCDB (Dew point 1.0%) | °C | 25.9 | (24.8 to 26.6) | 24.7 | (23 to 25.7) | -1.3 | (-2.4 to 0.1) | 26.9 | (24.4 to 29) | 0.9 | (-1.7 to 2.4) | 30.1 | (26.6 to 33.8) | 4.2 | (0.6 to 7.2)
Humidity Ratio 0.4% | g/kg | 11.9 | (10.5 to 13.1) | 12.8 | (11.2 to 13.9) | 0.8 | (0.4 to 1.4) | 13.2 | (11.6 to 14.6) | 1.3 | (0.9 to 1.8) | 13.4 | (11.9 to 15.2) | 1.5 | (0.8 to 2.1)
Humidity Ratio 1.0% | g/kg | 11.3 | (9.9 to 12.5) | 12.1 | (10.6 to 13.3) | 0.8 | (0.3 to 1.3) | 12.6 | (10.8 to 14) | 1.3 | (0.7 to 1.9) | 12.8 | (11.1 to 14.5) | 1.4 | (0.8 to 2.1)
Enthalpy 0.4% | kJ/kg | 298.2 | (297.6 to 298.7) | 299.9 | (298.8 to 300.8) | 1.7 | (0.9 to 2.5) | 302.3 | (300.3 to 304.2) | 4.1 | (2.5 to 5.8) | 305.1 | (301.8 to 308.4) | 6.9 | (3.4 to 9.7)
MCDB (Enthalpy 0.4%) | kJ/kg | 30 | (29.6 to 30.5) | 32.3 | (31 to 33.3) | 2.3 | (1.3 to 3.3) | 34.9 | (33.5 to 37.3) | 4.9 | (3.1 to 7.2) | 37.9 | (34.2 to 41.3) | 7.8 | (5.1 to 11.4)
MCWS (Dry-bulb 0.4%) | m/s | 2.2 | (1.5 to 3.4) | 2.6 | (1.8 to 3.7) | 0.4 | (0 to 0.8) | 2.6 | (1.8 to 3.5) | 0.4 | (0 to 1) | 2.3 | (1.7 to 3.1) | 0.1 | (-0.5 to 0.4)
PCWD (Dry-bulb 0.4%) | ° | 186 | (145 to 216) | 189 | (143 to 219) | 2 | (-17 to 16) | 191 | (142 to 221) | 5 | (-9 to 24) | 189 | (137 to 224) | 2 | (-9 to 22)
ASHRAE Extreme Annual Design Conditions
Annual Max Dry-Bulb | °C | 31 | (30.6 to 31.7) | 33.2 | (32.2 to 34.1) | 2.2 | (1.2 to 3.2) | 35.9 | (34.3 to 38.1) | 4.8 | (3.1 to 7.1) | 38.8 | (35.4 to 42.3) | 7.7 | (5.1 to 11.4)
Annual Min Dry-Bulb | °C | -33.2 | (-34 to -32.4) | -29.8 | (-31.6 to -28.7) | 3.4 | (1 to 5.3) | -27.4 | (-29.4 to -25.3) | 5.8 | (3.7 to 7.9) | -23.6 | (-25.5 to -21.9) | 9.6 | (7.4 to 11.9)
Annual Max Wet Bulb | °C | 21.9 | (21.6 to 22.2) | 23.9 | (23 to 24.5) | 1.9 | (1.5 to 2.7) | 26.1 | (24.5 to 27.7) | 4.2 | (2.9 to 5.8) | 28.7 | (25.4 to 31.5) | 6.7 | (3.7 to 9.5)
5-Year Annual Max Dry-Bulb | °C | 32.6 | (32.2 to 33.2) | 34.9 | (34.3 to 36.1) | 2.3 | (1.1 to 3.7) | 37.9 | (36.3 to 40.3) | 5.4 | (3.2 to 7.7) | 40.7 | (37.4 to 44.5) | 8.1 | (5.4 to 12.2)
5-Year Annual Min Dry-Bulb | °C | -36.3 | (-37.4 to -35.6) | -33.5 | (-35.7 to -31.6) | 2.8 | (0.6 to 5.4) | -30.5 | (-32.1 to -27.8) | 5.8 | (3.1 to 8.6) | -26.8 | (-29.1 to -24.9) | 9.5 | (7 to 11.4)
Extreme Windspeed 1.0% | m/s | 7.3 | (4.5 to 9.7) | 7.6 | (4.4 to 10.5) | 0.2 | (-0.2 to 0.3) | 7.6 | (4.3 to 10.8) | 0.2 | (-0.3 to 0.4) | 7.5 | (4.3 to 10.6) | 0.2 | (-0.3 to 0.3)
Extreme Windspeed 2.5% | m/s | 6.6 | (4 to 8.6) | 6.8 | (3.9 to 9.5) | 0.2 | (-0.3 to 0.3) | 6.8 | (3.8 to 9.7) | 0.3 | (-0.3 to 0.5) | 6.8 | (3.9 to 9.5) | 0.2 | (-0.2 to 0.4)
Extreme Windspeed 5.0% | m/s | 5.9 | (3.6 to 7.7) | 6.1 | (3.5 to 8.6) | 0.2 | (-0.3 to 0.3) | 6.2 | (3.4 to 8.7) | 0.2 | (-0.2 to 0.5) | 6.2 | (3.5 to 8.5) | 0.2 | (-0.2 to 0.4)
Average Annual Precipitation | mm | 424 | (411 to 438) | 433 | (423 to 447) | 9 | (-3 to 19) | 449 | (431 to 473) | 26 | (-21 to 54) | 454 | (420 to 489) | 30 | (-6 to 76)
Maximum Annual Precipitation | mm | 624 | (594 to 645) | 666 | (584 to 771) | 42 | (-34 to 134) | 704 | (634 to 793) | 81 | (31 to 140) | 685 | (623 to 767) | 61 | (5 to 124)
Minimum Annual Precipitation | mm | 240 | (188 to 292) | 254 | (226 to 295) | 14 | (-37 to 65) | 247 | (212 to 300) | 7 | (-65 to 66) | 265 | (218 to 301) | 25 | (-12 to 89)
Standard Deviation Annual Pr. | mm | 93 | (77 to 105) | 97 | (73 to 125) | 4 | (-8 to 22) | 115 | (91 to 137) | 22 | (-9 to 41) | 111 | (91 to 135) | 18 | (9 to 34)
5-Year Annual Max Daily Pr. | mm | 41 | (38 to 44) | 43 | (39 to 48) | 1 | (-4 to 6) | 46 | (42 to 50) | 5 | (0 to 8) | 47 | (40 to 55) | 6 | (-3 to 15)
Note on A5: Cold Dry-Bulb Temperature 99.6% Average annual 0.4th percentile value of daily minimum dry-bulb temperatures
Note on A6: Cold Dry-Bulb Temperature 99.0% Average annual 1.0th percentile value of daily minimum dry-bulb temperatures
Note on A7: Cold Dew Point Temperature 99.6% Average annual 0.4th percentile value of daily dew point temperatures
Note on A8: Humidity Ratio 99.6% Average annual 0.4th percentile value of the daily humidity ratio
Note on A9: Mean Coincident Dry-bulb (DP 99.6%) Mean coincident dry-bulb temperature for the 0.4th percentile value of daily dew point temperature
Note on A10: Cold Windspeed 0.4% Annual average 99.6th percentile value of the cold month daily windspeed
Note on A11: Mean Coincident Dry-bulb (WS 0.4%) Mean coincident daily minimum temperature for the 99.6th percentile value of daily windspeed
Note on A12: Mean Coincident Windspeed (DB 99.6%) Mean coincident windspeed for the 0.4th percentile value of the daily minimum temperature
Note on A13: Prevailing Coincident Wind Dir. (DB 99.6%) Prevailing coincident wind direction for the 0.4th percentile value of daily minimum temperature
Note on A15: Warm Dry-Bulb Temperature 0.4% Average annual 99.6th percentile value of daily maximum dry-bulb temperatures
Note on A16: Warm Dry-Bulb Temperature 1.0% Average annual 99.0th percentile value of daily maximum dry-bulb temperatures
Note on A17: Warm Wet Bulb Temperature 0.4% Average annual 99.6th percentile value of daily wet bulb temperatures
Note on A18: Warm Wet Bulb Temperature 1.0% Average annual 99.0th percentile value of daily wet bulb temperatures
Note on A19: Mean Coincident Dry-Bulb (WB 0.4%) Mean coincident daily maximum temperature for the 99.6th percentile value of daily wetbulb temperature
Note on A20: Mean Coincident Dry-Bulb (WB 1.0%) Mean coincident daily maximum temperature for the 99.0th percentile value of daily wetbulb temperature
Note on A21: Mean Coincident Wet Bulb (DB 0.4%) Mean coincident daily wet bulb temperature for the 99.6th percentile value of daily maximum temperature
Note on A22: Mean Coincident Wet Bulb (DB 1.0%) Mean coincident daily wet bulb temperature for the 99.0th percentile value of daily maximum temperature
Note on A23: Mean Coincident Wet Bulb (DB 2.0%) Mean coincident daily wet bulb temperature for the 98.0th percentile value of daily maximum temperature
Note on A24: Warm Dew Point Temperature 0.4% Average annual 99.6th percentile value of daily dew point temperatures
Note on A25: Warm Dew Point Temperature 1.0% Average annual 99.0th percentile value of daily dew point temperatures
Note on A26: Mean Coincident Dry-Bulb (DP 0.4%) Mean coincident daily maximum temperature for the 99.6th percentile value of daily dew point temperature
Note on A27: Mean Coincident Dry-Bulb (DP 1.0%) Mean coincident daily maximum temperature for the 99.0th percentile value of daily dew point temperature
Note on A28: Humidity Ratio 0.4% Average annual 99.6th percentile value of the daily humidity ratio
Note on A29: Humidity Ratio 1.0% Average annual 99.0th percentile value of the daily humidity ratio
Note on A30: Enthalpy 0.4% Average annual 99.6th percentile value of the daily enthalpy
Note on A31: Mean Coincident Dry-Bulb (Enth 0.4%) Mean coincident daily maximum temperature for the 99.6th percentile value of daily enthalpy
Note on A32: Mean Coincident Windspeed (DB 0.4%) Mean coincident windspeed for the 99.6th percentile value of the daily maximum temperature
Note on A33: Prevailing Coincident Wind Dir. (DB 0.4%) Prevailing coincident wind direction for the 99.6th percentile value of the daily maximum temperature
Note on A35: Annual Maximum Dry-Bulb Temperature Average annual maximum daily maximum dry-bulb temperature
Note on A36: Annual Minimum Dry-Bulb Temperature Average annual minimum daily minimum dry-bulb temperature
Note on A37: Annual Maximum Wet Bulb Temperature Average annual maximum daily wet bulb temperature
Note on A38: 5-Year Annual Maximum Dry-Bulb Temperature 5-year return period annual maximum daily maximum dry-bulb temperature
Note on A39: 5-Year Annual Minimum Dry-Bulb Temperature 5-year return period annual minimum daily minimum dry-bulb temperature
Note on A40: Extreme Annual Windspeed 1.0% Average annual 99.0th percentile value of the daily windspeed
Note on A41: Extreme Annual Windspeed 2.5% Average annual 97.5th percentile value of the daily windspeed
Note on A42: Extreme Annual Windspeed 5.0% Average annual 95.0th percentile value of the daily windspeed
Note on A43: Average Total Precipitation Average annual total precipitation
Note on A44: Maximum Total Precipitation Maximum annual total precipitation
Note on A45: Minimum Total Precipitation Minimum annual total precipitation
Note on A46: Standard Deviation of Total Precip. Standard deviation of annual total precipitation
Note on A47: 5-Year Annual Maximum Precipitation 5-year return period annual maximum daily precipitation
Note on C2: ASHRAE variables calculated for the past (1971-2000)
Note on C3: Average of the 10 model ensemble of for the past
Note on D3: Range of the 10 model ensemble of for the past (10th and 90th percentiles of the ensemble are shown)
Note on E2: ASHRAE variables calculated for the 2020s (2011-2040)
Note on E3: Average of the 10 model ensemble of future scenarios for the 2020s
Note on F3: Range of the 10 model ensemble of future scenarios for the 2020s (10th and 90th percentiles of the ensemble are shown)
Note on G2: Differences in the ASHRAE variables between the 2020s and the past
Note on G3: Average of the 10 model ensemble of future scenarios for the 2020s
Note on H3: Range of the 10 model ensemble of future scenarios for the 2020s (10th and 90th percentiles of the ensemble are shown)
Note on I2: ASHRAE variables calculated for the 2050s (2041-2070)
Note on I3: Average of the 10 model ensemble of future scenarios for the 2050s
Note on J3: Range of the 10 model ensemble of future scenarios for the 2050s (10th and 90th percentiles of the ensemble are shown)
Note on K2: Differences in the ASHRAE variables between the 2050s and the past
Note on K3: Average of the 10 model ensemble of future scenarios for the 2050s
Note on L3: Range of the 10 model ensemble of future scenarios for the 2050s (10th and 90th percentiles of the ensemble are shown)
Note on M2: ASHRAE ariables calculated for the 2080s (2071-2100)
Note on M3: Average of the 10 model ensemble of future scenarios for the 2080s
Note on N3: Range of the 10 model ensemble of future scenarios for the 2080s (10th and 90th percentiles of the ensemble are shown)
Note on O2: Differences in the ASHRAE variables between the 2080s and the past
Note on O3: Average of the 10 model ensemble of future scenarios for the 2080s
Note on P3: Range of the 10 model ensemble of future scenarios for the 2080s (10th and 90th percentiles of the ensemble are shown)

## About This File
About This File
File Description
This file (version: 1.1) contains past and future projections of selected ASHRAE Handbook
Climatic Design Variables calculated from climate model data for Calgary International Airport.
Further information about the variables in the rows can be seen by hovering over the row
headings (Column A) ASHRAE Variables tab. Design variables are grouped into three
categories following the ASHRAE Handbook convention:
- Heating and Humidification Design Conditions
- Cooling, Dehumidification and Enthalpy Design Conditions
- Extreme Annual Design Conditions
Methods and more information
These ASHRAE Design Conditions are calculated using climatic information obtained from an
ensemble of 10 global climate models selected for Western Canada (Cannon, 2015). Daily
maximum and minimum dry-bulb temperature and daily precipitation are obtained from
bias-corrected (BCCAQv2) CMIP5 climate models (Cannon et al., 2015). Surface pressure,
specific humidity, windspeed, and wind direction are obtained from GCMs interpolated to
the BCCAQv2 resolution (about 10 km). For this location a time series for each variable
is obtained from the nearest model grid cell. Additional variables required for the
ASHRAE Design Conditions including dew point temperature, wet bulb temperature, and
enthalpy are calculated from the available climate model data following the procedures
described in Stull (2000).
For a detailed description of BCCAQv2 see:
https://pacificclimate.org/data/statistically-downscaled-climate-scenarios
The 2020s, 2050s, and 2080s columns summarize information averaged over the 30-year
period, based on the future values and future changes according to the average,
10th percentile, and 90th percentile from the 10-model ensemble. The percentiles are
provided to encapsulate the range of plausible future change under the RCP8.5
(high emissions) scenario.
References
Cannon, A.J.,Sobie, S.R., and Murdock, T.Q. (2015) Bias correction of GCM
precipitation by quantile mapping: How well do methods preserve changes in
quantiles and extremes? J. Clim., 28, pp. 6938-6959
Cannon, A.J. (2015) Selecting GCM scenarios that span the range of changes
in a multimodel ensemble: application to CMIP5 climate extremes indices
J. Clim. 28, pp. 1260-1267
Stull, R. (2000) Meteorology for Scientists and Engineers. Brooks/Cole, 502 pp